Supplementary file for

Indoor Thermal Environment Improvement Based on Switchable Radiation/Convection-Combined Intermittent Heating: Comparison between Conventional Terminals and Integrated Novel Terminal

Hongli Sun a,e, Yifan Wu b,d,*, Borong Lin b,d,*, Mengfan Duan c,d, Zixu Yang b,d, Hengxin Zhao b,d, Ziliang Wei b,d,Shenfei Yu a, Songjun Li a, Junkang Song a

a College of Architecture and Environment, Sichuan University, Chengdu 610065, China

b Department of Building Science, Tsinghua University, Beijing 100084, China

c School of Energy and Environment, Southeast University, Nanjing 211189, China

d Key Laboratory of Eco Planning & Green Building, Ministry of Education, Tsinghua University, Beijing 100084, China

e State Key Laboratory of Intelligent Construction and Healthy Operation and Maintenance of Deep Underground Engineering, Sichuan

University, Chengdu 610065, China

*Corresponding authors.

E-mail addresses: wuyf97@126.com (Y. Wu), linbr@tsinghua.edu.cn (B. Lin).

Table S1

Description of components used in the radiant-convective terminal.

| Locations | Components | Description |
| --- | --- | --- |
| Indoor terminal | Heat exchangers | Material: Aluminum Size: 81 cm × 11 cm × 0.5 cm (L × H × W) Number: 4 pieces |
|  | FHPs | Material: Aluminum Size: 9 cm × 97 cm × 0.5 cm (L × H × W) Number: 9 pieces Charge: acetone (filling rate: 20%) Surface: silicon grease (emissivity: ~0.95) |
|  | Fins | Material: Aluminum Size: 0.5 cm × 11 cm × 0.2 mm (L × H × W), 540 pieces Fin spacing: 1.5 mm |
|  | Fans | Type: cross-flow fan Size: 30 cm × 5 cm × 5 cm, length of air inlet 28.6 cm Speed: 0-2000 rpm Air volume: 0-300 m3 h-1 Sound: 30 dB |
|  | Air Outlet | Size: 75 cm × 3 cm (L × H) |
| Outdoor unit | Compressor | Type: scroll compressor (SFES-34H345AY1) Displacement: 14.6 cm3 |
|  | Refrigerant | Type: R134a Charge: 1.2 kg |
|  | Heat exchanger | Copper pipe: length, external diameter, inner diameter of 36.4 m, 7 mm, and 6 mm, respectively Pipe spacing: 20 mm Path: 2 Fin thickness: 0.1 mm Fin spacing: 1.8 mm |